## Sheet1
location_id | formula | name | description
KO-91 | +(KO-11)+(KO-12)+(KO-13)+(KO-14)+(KO-15)+(KO-16)+(KO-17)+(KO-18)+(KO-19)+(KO-32)+(KO-34)+(KO-AD) | KO-91 | Total net Ex-bus injection by Korba STPS(Main)
KO-94 | -(KO-01)-(KO-02)-(KO-03)-(KO-04)-(KO-05)-(KO-06)-(KO-AD) | KO-94 | KORBA STG 1&2 GTs GEN.
KO-95 | -(KO-31) | KO-95 | KORBA STG 3 GT GEN.
KO-96 | +(KO-94)+(KO-95) | KO-96 | Sum of GT meters of Stage I,II&III.
KO-97 | 1*(KO-91)*(KO-94)/(KO-96) | KO-97 | Ex-bus total generation of KORBA 1&2.
KO-98 | 1*(KO-91)*(KO-95)/(KO-96) | KO-98 | Ex-bus total generation of KORBA 3.
KO-99 | (KO-91)+(KO-95) | KO-99 | Ex-bus total generation of KORBA 3(EXCLUDING tt-4).
MP-VI | +(VI-31)+(VI-33) | MP-VI | Total Waidhan drawal from VSTPS
VI-IC | +(VI-09)+(VI-10)+(VI-51)-(VI-43)-(VI-44)-(VI-52) | VI-IC | ACTUAL 400/132KV TRANSFORMER LOSS
VI-HV | +(VI-43)+(VI-44)+(VI-52) | VI-HV | TOTAL HV SIDE OF ICT1&2 AT VSTPS
VI-WI | 1*(VI-IC)*(LO-AD)/(VI-HV) | VI-WI | % LOSS OF ICT
MP-LO | 1*(MP-VI)*(VI-WI)/(LO-AD) | MP-LO | Loss apportioned from Waidhan drawal
VI-AJ | +(MP-LO) | VI-AJ | SUM OF ADJUSTMENT VALUE AND T'XMER LOSS OF VSTPS
VI-81 | +(VI-11)+(VI-12)+(VI-13)+(VI-14)+(VI-15)+(VI-16)+(VI-17)+(VI-18)+(VI-19)+(VI-31)+(VI-33)+(VI-37)+(VI-38)+(VI-39)+(VI-40)+(VI-45)+(MP-LO) | VI-81 | Sub-total-1 net Ex-bus injection by Vindhyachal STPS(Main)
VI-82 | +(VI-47)+(VI-49)-(VI-65)-(VI-66)+(RE-80) | VI-82 | Sub-total-2 net Ex-bus injection by Vindhyachal STPS(Main)
VI-91 | +(VI-81)+(VI-82) | VI-91 | Total net Ex-bus injection by Vindhyachal STPS(Main)
VI-71 | (RE-80) | VI-71 | Sub-total-1 net Ex-bus injection by Vindhyachal STPS(Check)
VI-72 | (RE-80) | VI-72 | Sub-total-2 net Ex-bus injection by Vindhyachal STPS(Check)
VI-92 | (RE-80) | VI-92 | Total net Ex-bus injection by Vindhyachal STPS(Check)
VI-93 | -(VI-01)-(VI-02)-(VI-03)-(VI-04)-(VI-05)-(VI-06)+(RE-80) | VI-93 | Stage-I GT meter readings
VI-94 | -(VI-07)-(VI-08) | VI-94 | Stage-II GT meter readings
VI-98 | -(VI-41)-(VI-42)-(RE-80) | VI-98 | Stage-III GT meter readings
VI-95 | +(VI-93)+(VI-94)+(VI-98) | VI-95 | sum of GT meters of Stage I,II&III
VI-96 | 1*(VI-91)*(VI-93)/(VI-95) | VI-96 | Ex-bus total generation of VSTPS I
VI-97 | 1*(VI-91)*(VI-94)/(VI-95) | VI-97 | Ex-bus total generation of VSTPS II
VI-99 | 1*(VI-91)*(VI-98)/(VI-95) | VI-99 | Ex-bus total generation of VSTPS III
KW-91 | +(KW-11)+(KW-12)+(KW-13)+(KW-14)+(KW-15)+(KW-16)+(KW-17)+(KW-18)+(KW-AD)-(RE-80) | KW-91 | Total net Ex-bus injection by Kawas GPS(Main)
KW-92 | -(KW-21)-(KW-22)-(KW-23)-(KW-24)-(KW-25)-(KW-26)-(KW-27)-(KW-28) | KW-92 | Total net Ex-bus injection by Kawas GPS(Check)
GA-91 | +(GA-11)+(GA-12)+(GA-13)+(GA-14)+(GA-AD) | GA-91 | Total net Ex-bus injection by Gandhar GPS(Main)
GA-92 | -(GA-21)-(GA-22)-(GA-23)-(GA-24) | GA-92 | Total net Ex-bus injection by Gandhar GPS(Check)
SP-91 | +(SP-11)+(SP-12)+(SP-13)+(SP-14)-(SP-30)-(SP-32)+(SP-AD)+(SP-25) | SP-91 | Total net Ex-bus injection by SIPAT NTPC(Main)
SP-92 | +(SP-21)+(SP-22)-(SP-23)-(SP-24)+(SP-31)+(RE-80)+(RE-80)-(SP-26) | SP-92 | Total net Ex-bus injection by SIPAT NTPC(Check)
SP-93 | +(SP-01)+(SP-02)+(SP-03)+(SP-04)+(SP-05)+(SP-30)+(SP-32)-(SP-83)+(RE-80) | SP-93 | Total net Ex-bus injection by SIPAT NTPC(STAND_BY)
SP-94 | +(SP-04)+(SP-05) | SP-94 | Adjustment value for SIPAT
SP-95 | +(SP-01)+(SP-02)+(SP-03)+(RE-80) | SP-95 | SIPAT GT-04 DIFF.
SP-96 | +(SP-94)+(SP-95) | SP-96 | TOTAL SUM OF SIPAT GT-01 & GT-4&5 GENERATION
SP-97 | 1*(SP-91)*(SP-94)/(SP-96) | SP-97 | APPORTIONED SIPAT GT-4&5 GENERATION
SP-98 | 1*(SP-91)*(SP-95)/(SP-96) | SP-98 | APPORTIONED SIPAT GT-01 GENERATION
SP-99 | +(SP-11)+(SP-12)+(SP-13)+(SP-14)+(SP-25) | SP-99 | TEST
MD-91 | (MD-21)+(MD-22)+(MD-23)+(MD-24)+(MD-27)+(MD-29) | MD-91 | MOUDA INJECTION(STG-1)
MD-93 | -(MD-01)-(MD-03)-(MD-02)-(MD-04) | MD-93 | MOUDA GT-1 AND GT-2 GEN
MD-94 | +(MD-06)-(MD-05)-(MD-07)-(MD-08)+(MD-AD) | MD-94 | MOUDA GT-3(STG-2) GEN
MD-95 | -(MD-01)-(MD-03)-(MD-02)-(MD-04)+(MD-06)+(MD-AD)-(MD-05)-(MD-07)-(MD-08) | MD-95 | MOUDA GT-1 AND GT-2 AND GT-3 GEN
MD-96 | 1*(MD-91)*(MD-93)/(MD-95) | MD-96 | MOUDA STG-1 FIRM GEN
MD-97 | 1*(MD-91)*(MD-94)/(MD-95) | MD-97 | MOUDA STG-2 INFIRM GEN OF UNIT-3
KA-94 | -(KA-01)-(KA-02)-(KA-03)-(KA-04)+(KA-AD) | KA-94 | Total net injection by KAPS 1&2
KA-95 | -(KA-06) | KA-95 | Total net injection by KAPS 3&4
KA-91 | -(KA-01)-(KA-02)-(KA-03)-(KA-04)-(KA-06)+(KA-AD) | KA-91 | Total net Ex-bus injection by Kakkarpar APS(Main)
KA-92 | +(KA-11)+(KA-12)+(KA-13)+(KA-14) | KA-92 | Total net Ex-bus injection by Kakkarpar APS(Check)
KA-93 | -(KA-21)-(KA-22)-(KA-23)-(KA-24)-(KA-25)-(KA-26)-(KA-27)-(KA-28) | KA-93 | Total net Ex-bus injection by Kakkarpar APS(Stand-by)
TA-91 | -(TA-01)-(TA-02)-(TA-03)-(TA-04)+(RE-80) | TA-91 | Total net Ex-bus injection by Tarapur APS 1&2(Main)
TA-92 | +(TA-11)+(TA-12)+(TA-13)+(TA-14) | TA-92 | Total net Ex-bus injection by Tarapur APS 1&2(Check)
TA-93 | -(TA-21)-(TA-23)-(TA-25)-(TA-27)-(TA-28) | TA-93 | Total net Ex-bus injection by Tarapur APS 1&2(Stand-by)
TA-94 | -(TA-05)-(TA-06)-(TA-07)-(TA-08)-(TA-81)+(TA-AD)-(TA-82)-(TA-83) | TA-94 | Total net Ex-bus injection by Tarapur APS 3&4(Main)
TA-95 | -(TA-15)-(TA-16) | TA-95 | Total net Ex-bus injection by Tarapur APS 3&4(Check)
TA-96 | -(TA-30)-(TA-31)-(TA-32)-(TA-29)-(TA-51)-(TA-52) | TA-96 | Total net Ex-bus injection by Tarapur APS 3&4(Stand-by)
PE-91 | -(PE-01)-(PE-02)-(PE-03)-(PE-04)+(PE-AD) | PE-91 | Total net Ex-bus injection by Pench Hydro(Main)
PE-92 | -(RE-80)-(RE-80)-(RE-80)-(RE-80) | PE-92 | PENCH drawl adjustment for MP (Main)
SS-GE | +(SS-22)+(SS-23)+(SS-25)+(SS-26)+(SS-27)+(SS-29) | SS-GE | RBPH GENERATION
SS-91 | -(SS-01)-(SS-02)-(SS-03)-(SS-04)-(SS-05)-(SS-06)-(SS-11)-(SS-13)+(SS-AD) | SS-91 | TOTAL SSP GENERATION
SS-EG | +(RJ-07)+(RJ-08)+(GU-23)+(GU-25)+(MH-27)+(MH-28) | SS-EG | STAND-BY FICTIOUS METER OF SSP
RG-91 | +(RG-21)+(RG-22)+(RG-23)+(RG-24)+(RG-AD) | RG-91 | Sum of GT's and ST's at RGPPL
RG-93 | +(RG-25)+(RG-26)+(RG-27)+(RG-28) | RG-93 | Sum of Outgoing feeders at RGPPL_check
LK-91 | -(LK-20)-(LK-21)+(RE-80)+(RE-80)+(RE-80)+(LK-AD) | LK-91 | NET INJECTION FROM LANCO(PATHADI)-MAIN
AC-91 | +(CS-71)+(CS-72)+(AC-AD) | AC-91 | ACBIL GENERATION
AC-93 | +(AC-91)+(ST-03) | AC-93 | ACBIL FIRM GENERATION
BL-91 | -(PC-49)-(PC-48)+(BL-AD) | BL-91 | BALCO TOTAL GENERTOIN
CG-91 | +(CG-21)+(CG-23)+(CG-29)+(CG-31)+(CG-25)+(CG-27)+(CG-35)+(CG-33)+(CG-AD) | CG-91 | SUM OF CGPL MUNDRA(MAIN)
CG-92 | -(CG-22)-(CG-24)-(CG-30)-(CG-32)-(CG-26)-(CG-28) | CG-92 | SUM OF CGPL MUNDRA(CHECK)
MN-91 | -(MN-21)-(MN-23)-(MN-25)-(MN-27)(MN-AD) | MN-91 | MAHAN INJ
MN-93 | -(MN-01) | MN-93 | MAHAN GT-1 GENERATION FIRM
MN-94 | -(MN-02) | MN-94 | MAHAN GT-2 GENERATION INFIRM
MN-95 | -(MN-01)-(MN-02) | MN-95 | MAHAN GT-1 AND GT-2 GENERATION
MN-96 | 1*(MN-91)*(MN-93)/(MN-95) | MN-96 | NET FIRM INJECTION
MN-97 | 1*(MN-91)*(MN-94)/(MN-95) | MN-97 | NET INFIRM INJECTION
KS-91 | -(KS-15)-(KS-17)+(KS-AD) | KS-91 | KSP INJ
KS-93 | (KS-01)+(KS-03)-(KS-02) | KS-93 | UNIT-3 AND UNIT-4 INJECTION
KS-94 | (KS-04)-(KS-05) | KS-94 | UNIT-2
KS-95 | (KS-01)-(KS-02)+(KS-03)+(KS-04)-(KS-05) | KS-95 | KSK INJECTION
KS-96 | 1*(KS-91)*(KS-93)/(KS-95) | KS-96 | KSK FIRM INJECTION
KS-97 | 1*(KS-91)*(KS-94)/(KS-95) | KS-97 | KSK INFIRM INJECTION
CS-92 | +(CS-01)+(CS-03)-(CS-88)-(CS-89)-(CS-87)-(CS-24)-(CS-51)-(CS-52)-(CS-54)-(CS-55)-(RE-80)-(CS-82)-(CS-83)+(CS-13)+(CS-11)-(CS-21)+(PT-11)+(PT-12)+(CS-AD) | CS-92 | SUB Total Drawal by Chhattisgarh (Main)
CS-93 | +(CS-65)+(CS-66)-(PC-28)+(CS-15)+(CS-17)+(CS-19)+(NS-96)-(CS-23)-(WR-26)-(CS-86)+(CS-34)+(CS-35) | CS-93 | SUB TOTAL-2 OF CSEB
CS-91 | +(CS-92)+(CS-93) | CS-91 | TOTAL DRAWAL OF CSEB
DD-91 | +(GU-81)+(GU-82)+(GU-88)+(GU-87)-(DD-51)-(DD-52)+(DD-61)+(DD-63)+(DD-AD) | DD-91 | Total Drawal by Daman&Diu (Main)
DD-DW | +(RE-80)+(RE-80) | DD-DW | SUM OF DALWADA AND DABHEL-DALWAD SEMS
DN-91 | -(DN-73)-(DN-74)+(RE-80)+(RE-80)-(DN-71)-(DN-72)+(RE-80)+(DN-AD)-(DN-79)-(DN-80)+(DN-87)+(DN-86)+(GG-76)+(GG-78)+(PR-52) | DN-91 | Total Drawal by Dadra&Nagarhaveli (Main)
GU-93 | -(GU-26)-(GU-27)-(GU-21)-(GU-22)-(GU-24)+(SS-21)-(GU-51)-(GU-52)-(GU-53)-(GU-54)-(GU-55)-(GU-56)-(GU-58)-(GU-59)-(GU-60)-(GU-61)-(GU-62)+(TA-27)-(GR-13)-(GR-14) | GU-93 | Partial drawal by GEB(Main)
GU-94 | -(GU-64)-(GU-65)+(TA-28)-(GU-81)*10000/9602-(GU-82)*10000/9602-(GU-88)*10000/9602-(GU-87)*10000/9602-(GU-68)-(GU-69)-(GU-70)+(RE-80)+(RE-80)+(RE-80)+(RE-80)+(GG-31)+(GG-32)+(GG-33)+(GG-34)+(SS-27)+(RE-80) | GU-94 | Partial drawal by GEB(main)
GU-NR | +(RE-80)+(RE-80) | GU-NR | LOSS CREDIT GIVEN TO GUVNL FOR WHEELING CENTRAL SECTOR POWER TO NR BY USING SOJA-KANSARI(CREDIT IS GIVEN ON TOTAL POWER FLOW THROUGH 400KV ZERDA-KANKROLI&ZERDA-BHINMAL)
SU-91 | +(SU-11)+(SU-12)+(RE-80)+(RE-80) | SU-91 | Net Sugen injection to WR grid
SU-93 | -(SU-21)-(SU-22) | SU-93 | CHECK INJECTION SET OF SUGEN
GU-95 | -(GU-28)-(GU-29)-(SU-91)-(GU-49)-(GU-50)-(GR-15)-(GR-16)-(GU-32)-(GU-31)-(AP-21)-(AP-23)-(GG-94)-(GG-95) | GU-95 | Partial drawal by GEB(main)
GU-96 | -(GG-92)-(GG-93)-(GG-16)-(GG-17)+(GG-08)+(GG-09)+(GG-12)-(GG-13)+(GR-17)+(GR-18)-(GG-51)-(GG-46)-(GG-47)-(GG-48)-(GG-49)-(GG-52)-(GG-53)-(GG-50)-(GG-43)-(GG-44) | GU-96 | Partial drawal by GEB(main)
GU-97 | -(GG-54)-(GG-55)-(AP-11)-(AP-13)-(GG-62)-(AP-15)-(AP-17)-(GG-63)-(GG-64)-(GG-65)+(PT-15)+(PT-17)+(GU-AD)+(GR-19)+(GR-20) | GU-97 | GUJRAT DRAWAL FROM MUNDRA
GU-98 | -(GG-72)-(GG-73)-(AP-25)-(AP-27)-(PC-14)-(PC-13)-(TT-01)-(TT-02)-(MR-55)-(MR-56)+(RE-80)+(RE-80) | GU-98 | GUJRAT DRAWAL FROM MUNDRA
GU-91 | +(GU-93)+(GU-94)+(GU-95)+(GU-96)+(GU-97)+(GU-98) | GU-91 | Total Drawal by Gujarat (Main)
MP-93 | +(MP-01)+(MP-03)+(MP-05)+(MP-07)+(MP-09)+(MP-23)+(MP-24)-(MP-30)-(MP-31)-(MP-32)-(MP-33)-(MP-67)-(MP-34)-(MP-35)+(RJ-10)+(MP-11)+(MP-13)+(MP-19)-(MP-68)+(MP-71) | MP-93 | Partial drawal by MPSEB(Main)
MP-94 | -(MP-36)-(MP-37)-(MP-38)-(MP-56)-(MP-57)-(MP-85)+(VI-31)+(VI-33)-(MP-51)+(PE-21)+(PE-23)+(MP-AD)+(RJ-09)-(MP-52)-(MP-53)-(MP-65)-(MP-66)+(MP-58)+(MP-LO)+(MB-11) | MP-94 | Partial drawal by MPSEB(main)
MP-95 | -(RJ-01)+(IT-01)-(MP-54)+(PC-21)+(RJ-03)-(MP-89)+(MB-13)+(MB-15)+(MB-17)+(RJ-21)*100/96+(IT-03)+(PC-69)+(PC-71)+(PC-89)+(MR-26)+(MR-34)+(MR-36)+(MR-38)+(MR-48) | MP-95 | Partial drawal by MPSEB(main)
MP-96 | -(MP-84)-(MP-90)-(DM-23)-(DM-24)-(DM-25)-(DM-26)-(MB-23)-(MB-24)-(MB-25)-(MB-26)-(RE-80)+(MB-19)-(MB-37)-(MB-39)-(MB-55)-(MB-56)-(UP-33)*100/96-(MB-81)+(BD-12)+(MP-97) | MP-96 | MP DRAWAL
MP-91 | +(MP-93)+(MP-94)+(MP-95)+(MP-96) | MP-91 | Total Drawal by Madhya Pradesh (Main)
MH-93 | -(MH-21)-(MH-22)-(MH-29)-(MH-30)-(MH-25)-(MH-26)+(SS-23)-(MH-54)-(MH-55)-(MH-31)+(TA-21)+(TA-23)+(MA-01)+(MA-02)+(MA-03)+(GO-51)*10000/9679+(GO-52)*10000/9679-(MH-44)-(MH-46)-(MM-12) | MH-93 | Partial drawal by MSEB(Main)
MH-94 | +(MH-01)+(MH-03)-(MH-58)-(MH-38)-(MH-39)-(MH-34)-(MH-37)+(SS-29)-(MM-32)-(MM-33)-(MH-57)+(PE-22)+(PE-24)+(WR-84)+(WR-85)-(MH-80)-(MH-81)+(MH-AD)-(MH-65)-(MH-66) | MH-94 | Partial drawal by MSEB(main)
MH-95 | +(RG-21)+(RG-22)+(RG-23)+(RG-24)-(MH-76)-(MH-77)-(MH-43)-(MH-45)-(MM-13)-(MM-14)-(MM-17)-(MM-19)+(MM-47)+(MM-49)-(MM-20)-(MM-21)-(MH-47)-(MH-48)-(MH-49)-(MH-50) | MH-95 | MSEDCL FICTMTR
MH-96 | -(MM-26)-(MM-27)-(MM-28)-(MM-29)-(MM-36)-(MM-37)-(MH-32)-(MH-33)-(MM-38)-(MM-39)-(MM-52)-(MM-54)-(PG-81)-(PG-82)+(MM-61)-(PG-41)-(PG-40)-(PC-19)-(PC-20)+(MA-04) | MH-96 | AKOLA DRAWAL OF MSEB
MH-97 | +(PR-26)+(PR-27)+(PR-31)+(PT-21)+(PT-22)+(PR-42)+(PR-43)+(PG-12) | MH-97 | PARTIAL DRAWAL OF MSEB
MH-91 | +(MH-93)+(MH-94)+(MH-95)+(MH-96)+(MH-97) | MH-91 | Total Drawal by Maharashtra (Main)
GO-91 | +(GO-01)+(GO-03)-(GO-51)-(GO-52)+(GO-05)+(GO-AD) | GO-91 | Total Drawal by Goa (Main)
PG-91 | -(WR-84)-(WR-85)+(VI-37)+(VI-38)+(VI-39)+(VI-40)+(RE-80)+(CM-11)+(CM-12) | PG-91 | Total Drawal by POWERGRID at HVDC
SR-91 | +(WR-31)+(WR-32)+(MM-44)+(MM-57)+(PG-76)+(PG-77)+(SR-AD)+(PC-77)+(PC-78) | SR-91 | Total Import from Souther Region(Main)
SR-92 | +(WR-33)+(WR-34)+(SR-11)+(SR-12)+(PG-78)+(PG-79) | SR-92 | Total Import from Souther Region(Check)
SR-93 | -(WR-33)-(WR-34)+(SR-11)+(SR-12)+(PG-78)+(PG-79) | SR-93 | RAMAGUNDAM DRAWAL
NR-94 | -(PG-48)-(PG-49)+(RJ-21)-(UP-33)-(PC-30)-(PC-31)+(CH-25)-(CH-28)-(PG-87)-(PG-88)-(MR-01)-(MR-02)-(MR-03)-(MR-04)-(MR-69)-(MR-74)-(MR-75) | NR-94 | NR Sub drawal
NR-93 | -(VI-17)-(VI-18)+(AU-06)+(AU-05)-(MP-77)+(NR-AD)-(MP-54)+(PC-21)-(MP-49)-(GU-49)-(GU-50)-(MP-89)-(AP-11)-(AP-13)-(AP-15)-(AP-17)-(RE-80)-(AP-25)-(AP-27)+(NR-94) | NR-93 | MAIN WR-NR EXCHANGE
NR-91 | +(VI-27)+(VI-28)-(AU-16)+(MP-49)-(AU-15)+(RE-80)-(RS-01)-(RS-03)+(MP-77)-(RS-06)-(RS-08)+(MP-89)+(AP-12)+(AP-14)+(AP-16)+(AP-18)+(MB-71) | NR-91 | Total Import from Northern region(Main)
NR-92 | +(NR-11)+(NR-12)-(MP-52)-(MP-53)+(UP-01)-(NR-AD)+(RS-01)+(RS-03)+(UP-02)+(RS-06)+(RS-08)-(MP-89)-(MO-12)-(MO-11)-(MO-15)-(MO-16)+(RI-11)+(PG-50)+(PG-51) | NR-92 | Total Import from Northern region(Check)
NR-RV | -(NR-92) | NR-RV | NR-92 REVERSED
ER-91 | +(OR-56)+(OR-57)+(OR-58)+(WR-57)+(WR-86)+(WR-41)+(WR-42)+(WR-58)+(WR-82)+(CH-19)+(WR-73)+(WR-74)+(ER-AD)+(PC-15)+(WR-89)+(WR-90)+(WR-03)+(WR-04) | ER-91 | Total Import from Eastern Region(Main)
ER-92 | +(RE-80)+(CS-54)+(CS-55)+(WR-36)+(WR-38)+(SP-44)+(SP-45)+(WR-47)+(WR-48) | ER-92 | Total Import from Eastern Region(Check)
NT-91 | +(KO-91)+(VI-91)+(KW-91)+(GA-91)+(SP-91)+(MD-91)+(VI-V4)+(VI-V5)+(RE-80)+(SO-91)+(LA-91)+(KH-91)+(GD-91) | NT-91 | NTPC TOTAL
NP-91 | +(TA-91)+(TA-94)+(KA-91) | NP-91 | NPC TOTAL
HY-91 | +(SS-91)+(PE-91) | HY-91 | HYDRO TOTAL
IP-92 | +(JD-99)+(LK-91)+(NS-91)+(AC-91)+(RG-91)+(BL-91)+(CG-91)+(DC-91)+(DG-91)+(MN-91)+(KS-91)+(SA-91)+(RE-80)+(EM-91)+(KB-91)+(DB-91)+(JY-91)+(GM-91)+(DW-91) | IP-92 | IPP TOTAL(PART1)
IP-93 | +(RK-91)+(MB-91)+(JH-91)+(SK-91)+(TR-91)+(MA-91)+(AR-91)+(OS-91)+(AM-91) | IP-93 | IPP TOTAL(PART2)
IP-91 | +(IP-92)+(IP-93) | IP-91 | IPP TOTAL
IR-91 | +(ER-91)+(NR-93)-(SR-91) | IR-91 | INTER REGIONAL TOTAL
SD-91 | +(GU-91)+(MP-91)+(MH-91)+(GO-91)+(DD-91)+(DN-91)+(PG-91)+(HZ-91)+(BR-91) | SD-91 | STATE DRAWAL W/O CSEB
IG-91 | +(NT-91)+(NP-91)+(HY-91)+(IP-91) | IG-91 | TOT WR GENERATION W/O I/R
IN-93 | +(KO-91)+(VI-91)+(KW-91)+(GA-91)+(KA-91)+(TA-91)+(SS-91)+(PE-91)+(TA-94)+(SP-91)+(JD-99)+(LK-91)+(CG-91)-(SR-91)+(NR-93)+(ER-91)+(NS-91)+(AC-91)+(RG-91)+(BL-91) | IN-93 | INJECTON-1
IN-94 | +(DC-91)+(VI-V5)+(MN-91)+(MD-91)+(KS-91)+(SA-91)+(RE-80)+(EM-91)+(VI-V4)+(KB-91)+(DB-91)+(JY-91)+(DG-91)+(GM-91)+(DW-91)+(RK-91)+(MB-91)+(JH-91)+(SK-91) | IN-94 | INJECTION-2
IN-97 | +(TR-91)+(LA-91)+(GD-91)+(KH-91)+(MA-91)+(AR-91)+(OS-91)+(AM-91)+(RE-91)+(GI-91)+(GI-94)+(IX-91) | IN-97 | INJECTION3
IN-91 | +(IN-93)+(IN-94)+(IN-97) | IN-91 | Total Injection by Western Region
DR-91 | +(CS-91)+(GU-91)+(MH-91)+(MP-91)+(GO-91)+(DD-91)+(DN-91)+(PG-91)+(HZ-91)+(BR-91) | DR-91 | Total Drawal by Western Region Beneficiaries
IN-95 | +(KO-91)+(VI-91)+(KW-91)+(GA-91)+(KA-91)+(TA-91)+(SS-91)+(PE-91)+(TA-94)+(SP-91)+(JD-99)+(LK-91)+(NS-91)+(AC-91)+(RG-91)+(BL-91)+(CG-91)+(DC-91)+(SO-91)+(MN-91) | IN-95 | INJECTION
IN-96 | (MD-91)+(KS-91)+(SA-91)+(JH-91)+(EM-91)+(VI-V4)+(KB-91)+(DB-91)+(JY-91)+(DG-91)+(GM-91)+(DW-91)+(RK-91)+(MB-91)+(SK-91)+(VI-V5) | IN-96 | INJECTION2
DR-92 | +(MH-91)+(MP-91)+(GO-91)+(GU-91)+(CS-91)+(DD-91)+(DN-91)+(PG-91)+(SR-91)-(NR-93)-(ER-91)+(HZ-91)+(BR-91) | DR-92 | OLD DRAWAL FORMULA
IN-92 | (IN-95)+(IN-96)+(IN-97) | IN-92 | OLD INJECTION FORMULA
LO-91 | +(IN-92)-(DR-92) | LO-91 | Total system loss in Western Region
LO-00 | 100*(LO-91)*(LO-AD)/(IN-92) | LO-00 | % LOSS
SA-91 | +(SA-17)+(SA-21)-(SA-15)-(SA-16)+(SA-AD)+(SA-23)+(SA-20)+(SA-29)+(SA-31) | SA-91 | SASAN INJ
ST-91 | -(ST-12)+(ST-AD) | ST-91 | SPECTRUM INJ
EM-91 | -(MM-22)-(MM-23)+(EM-AD) | EM-91 | EMCO INJECTION
MD-92 | (MD-25)+(MD-26)+(MD-28)+(MD-30) | MD-92 | MOUDA GEN
KB-91 | -(PC-41)-(PC-40)+(KB-AD) | KB-91 | KORBA WEST INJ
VI-V4 | -(VI-67)-(VI-68)(VI-59)+(VI-61)+(VI-73)+(VI-75)+(VI-AD) | VI-V4 | VIN STAGE IV DRAWAL
VI-IV | (RE-80) | VI-IV | VIN STAGE-4
VI-V5 | +(VI-65)+(VI-66)+(VI-67)+(VI-68)+(RE-80) | VI-V5 | VIN STAGE V DRAWAL
JY-91 | -(ST-51)-(ST-52)(JY-AD) | JY-91 | JAYPEE NIGRI INJECTION
HZ-91 | -(HZ-12)-(HZ-14)+(HZ-AD) | HZ-91 | HAZIRA DRAWAL
DG-91 | -(GG-70)-(GG-71) | DG-91 | DGEN GEN
GM-91 | -(CH-11)-(CH-12) | GM-91 | GMR CHHATTISGARH INJECTION
DW-91 | -(DW-21)-(DW-23)+(DW-AD) | DW-91 | DHARIWAL INFRA
MP-97 | +(MB-85)+(MB-86)+(PR-48)+(PR-50)-(MR-84)-(MR-85) | MP-97 | MP DRAWAL NEW FILE
VE-91 | +(LO-AD)-(LO-AD) | VE-91 | VIRTUAL ENTITY WR.